Could you send through drawing no K (30) 003 C2 which indicates the Komfort partitions? It isn’t in the tender package.

Drawing is L(30) 003 C2 as attached.

This is one of the internal door schedule drawings and details the 1hr fire rated Komfort Defence EI steel framed glazed partitions and double doors leading from the main entrance lobby  (and is fitted within Komfort Solid 60/60 Fire rated partition wall.)

Also, have you any drawings that will indicate how to access the site from the road, and also where we can set up our site welfare?

Part of the car park (which is accessed off Park Grove)  and an area around the pavilion will be made available for site set up. These areas will need to be made good afterwards and the health of safety arrangements agreed with the Council/ ANSA.

Contractors will have to provide their site set up proposals for agreement to ensure public safety. Note that pedestrian public access will need to be maintained from the metal gates into the park. See attached L000 rev A Site Location Plan A1 1-500

Can you suggest the finishes to the following for wall finishes:

G1 – Unpainted Fire Rated Plasterboard

G2 - Unpainted Fire Rated Plasterboard

G16 – White Washable Moisture Resistant Paint (W3 on drawing)

F1 - Unpainted Fire Rated Plasterboard

F6. – Unpainted Fire Rated Plasterboard

Also, for ceiling finishes I have assumed the Studio Green paint finish to all rooms detailed in the ceiling finishes section.

All washrooms, staff rooms, and kitchens to have white hygienic suspended ceiling tiles. All other rooms to have Studio Green paint colour matched ceilings.

Finally, there is no floor finish specified for F9 (Event Space) The date sheet suggests parquet flooring but there is no inclusion in the flooring finishes section. Is it excluded? Also, F7 & F8 don’t have a floor finish shown.

The parquet flooring is just the F2 LVT Planks laid in a herringbone pattern.

Is there a possibility of an extension to the current submission date, due to bank holidays in the middle of the tender period

No

Where will we be allowed to setup a compound area for the works (in the park or in the car park off Park Grove)

Either provided that safe access to the park is maintained for park users.

Is all site access to be via Park Grove or Park Vale Rd

Park Grove

Can you please advise the max width of access into park for deliveries

Via existing gated access off the Park Grove car park. If necessary, builders may opt to remove one gate post temporarily to allow wider access.

Is there a Form of Tender for completion

What other items need to be returned with the tender

All the tender documents are on the Town Council website here: South Park Pavilion Construction Tender - Macclesfield Town Council

Technical Drawings here: https://drive.google.com/drive/folders/1Ny9edYQXXN7_JUWOMKKa631naGDQ30rQ?usp=drive_link

Kitchen Confirmed kitchen layout, appliance specs

Kitchen layout and appliance specification needs to be provided by Andserv. There is no current ratings of individual equipment.

Mech Ratings of all mechanical items, ie condensors etc

Ratings of all mechanical equipment, condensers etc. can be found using the model reference which are noted on the layouts and the data sheets are available from the manufacturers website.

External Any external drawing

No external drawing has been produced currently. This will be completed and appended to the drawing pack as an addendum to the tender W/C 06/04/26.

DB Completed fuseboard drawings, Circuit design schedules - drawing seesm part done only

DB schematic has been produced to stage 3 detail as there was limited time for MEP design. Mains cables have been noted on the schematic and the contractor can provide a description of what has been allowed for - the technical design element will be completed prior to contract issue drawings.

Heaters Who is providing these, do we have a spec/model

Allow for electric radiant panel heaters as Thermatile by SPC, 500W panels. Allow for wall mounted electric panel heaters as Dimplex Q-Rad 1000W.